The important point is that this is not simply asking you to replace one REST endpoint with another. It defines several integration capabilities, and some of them may require OpenAccess REST APIs plus Lenel event infrastructure, while some are explicitly new scope requiring client approval.

The requirement says the OnGuard server has been upgraded and now exposes Lenel OpenAccess

The document also says Lenel/the authorized ACS integrator needs to provide or confirm the necessary licensing, Application ID, API versions, accounts, permissions, event setup, testing and cutover details

2. Mandatory baseline requirements

These are the capabilities that appear to be required for the migration.

A. Inventory and identifiers

The iBMS needs to obtain information about OnGuard objects such as:

Panels / Controllers, Readers, Doors,Alarms, I/O, Communication Servers

Names

IDs

Segments

Locations

This means your Java integration needs some form of inventory/discovery functionality.

But the actual API endpoints and fields need to come from the OpenAccess API version Lenel confirms.

B. Live status and alarms

This is one of the most important requirements.

The integration needs to obtain states such as:

Online / Offline

Communication:

Lost

Restored

Reader / Door:

Forced

Held

Tamper

Power / Voltage

Alarm:

Active

Restored

OnGuard | | status/event information v Java Integration | +--> Door status +--> Reader status +--> Controller status +--> Communication status +--> Alarm status

You will need Lenel to confirm whether each live status is obtained through OpenAccess REST polling, event delivery, or a combination of both.

3. Event feed requirement

The second mandatory requirement is the event feed.

The document specifically refers to:

- Access Granted

- Access Denied

- Access Granted (PIN)

- Access Denied (PIN)

- Emergency

- Area Control

- Category

It also mentions other recovery/access-related events.

This means your integration cannot just periodically call:

GET /events

and assume that's sufficient.

The document specifically refers to LS Event Context Provider, and page 5 says:

the LS Event Context Provider service must run on the same host as LS OpenAccess.

That is an important infrastructure requirement.

The architecture therefore appears closer to:

Lenel OnGuard

|

+----------+----------+

|                     |

v                     v

OpenAccess          Event Context

APIs                Provider

|                     |

+----------+----------+

You need Lenel to confirm the precise event subscription/delivery mechanism for your installed version.

4. Commands that replace existing legacy functionality

The document identifies some command/control functionality as confirmed baseline / legacy-equivalent.

An important example is:

Door control

The document specifically mentions:

Unlock Door

Therefore the migrated integration needs to preserve the existing ability to command a door where that functionality already existed.

Conceptually:

iBMS UI

|

| User clicks "Unlock"

v

Java Backend

|

| authorization check

| audit logging

v

OpenAccess

|

v

OnGuard

|

v

Door / Controller

This is a security-sensitive operation. I would not allow React/iBMS frontend code to call OpenAccess directly.

5. New functionality requiring client approval

The amber/new-scope section is particularly important.

The document says these capabilities are not part of the legacy baseline and require explicit client approval.

Reader mode/state change

Example mentioned:

SetMode

This could mean changing operational state/mode of a reader.

The requirement therefore distinguishes:

Existing functionality

-----------------------

Unlock Door

↓

Required migration

New functionality

-----------------

SetMode

↓

Requires client approval

Don't implement SetMode merely because OpenAccess supports it. The client must approve it.

6. Command-issued alarm acknowledgement

Another new requirement is alarm acknowledgement.

The document describes:

Command-issued alarm acknowledgement

and says it requires appropriate acknowledgements.

Conceptually:

Alarm generated

|

v

OnGuard

|

v

iBMS

|

Operator reviews alarm

|

v

Acknowledge

|

v

Java Backend

|

v

OpenAccess / supported interface

|

v

OnGuard

Again, this is explicitly outside the legacy baseline according to the document and requires client approval.

7. Identity/cardholder functionality is excluded by default

This is a very useful scope clarification.

The document says Identity / Credential admin is excluded unless separately approved.

That includes things like:

Create cardholder

Modify cardholder

Create badge

Modify badge

Create credential

Modify credential

Assign access levels

PIN management

So the Java implementation I described earlier for:

Create Cardholder

→ Create Badge

→ Assign Access Level

is not part of this particular MDD migration scope unless the client explicitly approves it.

Your main scope appears to be much more about:

Device Inventory

+

Live Device Status

+

Events

+

Alarms

+

Door Commands

rather than employee/cardholder administration.

8. Licensing requirement

This is one of the major unanswered items.

The RFI asks Lenel to confirm the permanent OpenAccess licence and a unique Application ID for MDD iBMS.

The document appears to say OpenAccess is a licensed feature requiring a unique Application ID and appropriate licensing.

So before development, you need Lenel/the ACS integrator to provide or confirm:

OpenAccess License

+

Unique MDD Application ID

+

OpenAccess API version

+

Integration account

+

Required permissions

Do not assume that because the OnGuard server exposes OpenAccess, your application is automatically licensed/authorized to use every capability.

9. API/version confirmation

The document asks Lenel to confirm:

exact deployed OnGuard version/build/hotfix and applicable OpenAccess API versions.

This is critical for your Java development.

You need something like:

OnGuard Version:

8.x.x

Build:

xxxxx

Hotfix:

xxxxx

OpenAccess API Version:

x.x

OpenAccess Base URL:

https://<server>/api/...

Authentication:

<confirmed mechanism>

Application ID:

<MDD-specific ID>

Only after you get this should you finalize your Java API client.

This is why I wouldn't recommend copying random OpenAccess endpoint examples from the internet—the API contract must match this installation.

10. Integration/service account

Lenel also needs to provide an integration account with appropriate:

Permissions

Segment access

Monitoring-zone access

Command permissions

This is important because your Java service account should follow least privilege.

For example:

MDD_OPENACCESS_SERVICE

|

+-- Read panel inventory       ✓

+-- Read reader inventory      ✓

+-- Read door state            ✓

+-- Receive events             ✓

+-- Receive alarms             ✓

+-- Unlock approved doors      ✓

+-- SetMode                    ? Client approval

+-- Acknowledge alarms         ? Client approval

+-- Modify cardholders         ✗

+-- Modify badges              ✗

That is much safer than giving the integration account unrestricted OnGuard administrator privileges.

11. Segment access is important

The document specifically asks Lenel to confirm:

segmentation status, the segment model for MDD phases/buildings, and the access required by the iBMS account.

This means your site may have multiple security segments corresponding to buildings/phases.

For example:

OnGuard

|

+-- Segment A

|      +-- Building A

|      +-- Readers

|      +-- Doors

|

+-- Segment B

|      +-- Building B

|      +-- Readers

|

+-- Segment C

+-- Building C

Your MDD account may need access only to selected segments.

Your Java integration therefore shouldn't assume:

getAllReaders();

returns every physical reader in the system.

The results may depend on the permissions and segment visibility of the OpenAccess account.

12. Infrastructure requirements

Page 5 contains several infrastructure confirmations.

The current system appears to have:

2 Application Servers

2 Database Servers

Communication Servers

OpenAccess / NGINX between

application and DB servers

The document asks Lenel/client to confirm the final hypervisor/platform hosting the application and database servers.

It also asks Lenel to confirm host assignment for each OpenAccess microservice, particularly because the:

Event Context Provider must be co-located with LS OpenAccess.

So this isn't just a Java coding exercise. There is also an infrastructure deployment requirement.

13. Test environment is required

The document asks for:

Test environment

Joint test procedure

Support contacts

Cutover plan

I strongly recommend not testing command APIs against production first, particularly:

Unlock Door

SetMode

Alarm Acknowledge

A suitable flow would be:

DEV

|

v

OpenAccess Test Environment

|

v

Test Panel / Reader / Door

|

v

Integration Testing

|

v

UAT

|

v

Production

14. What your Java application actually needs to implement

Based on these two pages, I would break your Java OpenAccess integration into approximately these modules:

lenel

|

+-- authentication

|      LenelAuthenticationClient

|      LenelTokenManager

|

+-- inventory

|      PanelClient

|      ReaderClient

|      DoorClient

|      AlarmPointClient

|

+-- status

|      DeviceStatusService

|      DoorStatusService

|

+-- event

|      LenelEventService

|      EventContextHandler

|      AccessEventProcessor

|

+-- command

|      DoorCommandService

|      SetModeService        [if approved]

|

+-- alarm

|      AlarmService

|      AlarmAcknowledgeService [if approved]

|

+-- mapping

|      LenelToMddMapper

|

+-- audit

LenelCommandAuditService

And the high-level architecture would be:

MDD / iBMS

|

+-----------+-----------+

|                       |

Monitoring               Commands

|                       |

v                       v

+---------------------------------------+

|          Java / Spring Boot           |

|                                       |

| Authentication / Token Management     |

| Inventory                             |

| Device Status                         |

| Event Processing                      |

| Alarm Processing                      |

| Command Service                       |

| Audit Logging                         |

+-------------------+-------------------+

|

| HTTPS

v

+---------------------+

| Lenel OpenAccess    |

+----------+----------+

|

+---------+---------+

|                   |

v                   v

REST APIs        Event Context

Provider

|                   |

+---------+---------+

|

v

OnGuard

|

+---------------+---------------+

|               |               |

Panels          Readers          Doors

|

Alarms