OnGuard

│

├── Integration Status

│

├── Building A

│   ├── Panel 01

│   │   ├── Main Entrance Reader

│   │   │   ├── Access Granted

│   │   │   └── Access Denied

│   │   ├── Server Room Reader

│   │   │   ├── Access Granted

│   │   │   └── Access Denied

│   │   └── ...

│   └── Panel 02

│

└── Event History

| OnGuard condition | Niagara Event Type | Niagara Reason |
| --- | --- | --- |
| Granted Access | ACCESS_GRANTED | Granted |
| Invalid Badge | ACCESS_DENIED | Invalid Badge |
| Inactive Badge | ACCESS_DENIED | Inactive Badge |
| Expired Badge | ACCESS_DENIED | Card Expired |
| Invalid Timezone | ACCESS_DENIED | Outside Schedule |
| Reader Locked | ACCESS_DENIED | Reader Locked |
| Access Denied | ACCESS_DENIED | Access Denied |
| Unknown/unsupported | ACCESS_DENIED | OnGuard event description |

Step 2: Create the OnGuard Network

You must establish the parent network that will house the reader devices.

- Open your Niagara Station slot sheet and navigate to the Drivers folder.

- Open the Palette side-bar and search for your specific OnGuard driver library.

- Drag and drop the OnGuardNetwork component into your Drivers folder.

- Open the property sheet of the new network and input your LenelS2 OnGuard server credentials:

  - Host IP/URL: The address of the OnGuard Application/Web Server.

  - API Port: Typically 8080 (HTTP) or 443 (HTTPS).

  - Authentication: Enter the OpenAccess API integration Username and Password created during the initial setup.

- Save the properties and verify the status changes to {ok} (signaling successful authentication with the OpenAccess layer).

Step 3: Run Device Discovery for Readers

Instead of manually typing in every reader's hardware configuration, you will pull them automatically from the OnGuard database.

- Double-click the OnGuardNetwork to open its default device manager view.

- Click the Discover button at the bottom of the manager screen.

- In the discovery filter pop-up, you can usually choose what object types to look for. Select Readers (or Panels, depending on how the driver groups hardware hierarchies) and click OK.

- The Niagara driver will send an API query (GET /openaccess/readers) to the OnGuard server.

- The top pane of the manager window will populate with a list of all physical and virtual readers configured in the OnGuard system.

Step 4: Add Readers to the Database

Once the discovery pane populates, you must explicitly move them into the station's active database.

- Highlight the desired readers in the top Discovered pane.

- Click the Add button at the bottom of the screen.

- An Add dialog box will appear. Review the following parameters:

  - Name: By default, this pulls the Reader Name from OnGuard (e.g., Front_Entry_Reader). You can keep this or customize it.

  - Type: Ensures it maps as an OnGuard Reader device type.

  - OnGuard ID / External ID: This is a crucial, read-only integer or GUID that matches OnGuard's internal database indexing. Do not change this.

- Click OK. The readers will drop into the lower Database pane, changing their status to {ok}.

The integration shall make the following door statuses from LenelS2 OnGuard available to Niagara:

- Door Open – indicates that the physical door contact is in the open state.

- Door Closed – indicates that the physical door contact is in the closed state.

- Door Forced Open – indicates that the door has been opened without a valid authorized access event or permitted unlock condition.

- Door Held Open – indicates that the door has remained open beyond the configured held-open time threshold in OnGuard.

Niagara shall receive these statuses as individual readable points/events and shall update them in near real time whenever the corresponding status changes in OnGuard.

Recommended Niagara point model:

Door

├── OpenStatus       Boolean

├── ClosedStatus     Boolean

├── ForcedOpenStatus Boolean

└── HeldOpenStatus   Boolean

A stronger functional-requirement statement would be:

The LenelS2 OnGuard integration shall expose each configured door's Open, Closed, Forced Open, and Held Open status to Niagara. Status changes shall be communicated to Niagara in near real time and shall reflect the current status maintained by the OnGuard system.

The LenelS2 OnGuard integration shall expose the status of configured readers and access-control controllers to Niagara. The integration shall make reader availability/health and controller communication/health status available as Niagara points and shall update the corresponding status whenever a change is detected in OnGuard.

Typical statuses can include:

Reader Status

- Online

- Offline

- Fault

- Tamper, if available

Controller Status

- Online

- Offline

- Communication Fault

- Tamper

- Power/Battery Fault, if available

For a shorter specification-style statement:

The integration shall make Reader Status and Controller Status from LenelS2 OnGuard available to Niagara in near real time.

If building a direct API integration using Niagara's HTTP/JSON capabilities.

- Initial Discovery: Niagara must execute an HTTP GET request to https://<onguard-server>:<port>/openaccess/config/panels and /openaccess/config/readers to discover all hardware IDs.

- Live Status Monitoring:

  - Polling Method: Niagara must send periodic HTTP GET requests to the /openaccess/status/panels endpoint to fetch the JSON array containing the health metrics.

  - WebSocket Method: Niagara opens a persistent secure WebSocket connection (wss://) to the OnGuard event stream. The integration parses incoming standard status event messages (e.g., Panel Offline, Reader Tamper).

The LenelS2 OnGuard integration shall expose Request-to-Exit (REX) input states and configured Emergency Input states to Niagara. The integration shall make the current input state and any associated alarm/fault condition available as Niagara points and shall update those points whenever the corresponding state changes in OnGuard.

For Request-to-Exit (REX), Niagara should be able to distinguish at least:

REX Status

- Normal / Inactive

- Active / Request-to-Exit Triggered

- Fault / Trouble, if supported

- Tamper, if supported

When the REX input is activated, the integration should update Niagara in near real time. The point should represent the actual state reported by OnGuard rather than Niagara independently inferring the condition from door activity.

For Emergency Inputs, the integration should support configured security or emergency input points such as emergency release, emergency door unlock, panic/duress input, fire interface input, or other designated alarm inputs, depending on the project configuration.

Recommended states are:

Emergency Input Status

- Normal

- Active / Alarm

- Restored / Normal

- Fault / Trouble

- Tamper, if available

- Unknown / Communication Lost

A recommended Niagara point structure is:

Door_101

├── REX

│    ├── Active

│    ├── Fault

│    └── Tamper

│

└── EmergencyInput

├── Active

├── Alarm

├── Fault

└── Tamper

For the functional specification, I would use this wording:

The integration shall make Request-to-Exit (REX) and Emergency Input states from LenelS2 OnGuard available to Niagara. The integration shall expose Normal/Inactive, Active/Alarm, Fault/Trouble, Tamper, and communication-loss states where supported by OnGuard. State changes shall be communicated to Niagara in near real time, and Niagara shall indicate an Unknown or Fault condition when the corresponding OnGuard input state cannot be reliably determined.

One important design point is that REX activation should be exposed as an input state, not treated as a security alarm by default. Emergency inputs, on the other hand, may need to generate Niagara alarms de

3. Niagara Point Configuration Requirements

To ensure these inputs behave correctly for building control and automation, they must be brought into Niagara using specific object structures:

| Input Component | Target Niagara Object | Expected States / Values | Technical Purpose in Niagara |
| --- | --- | --- | --- |
| Request-to-Exit (REX) | BooleanPoint | true (Active / Tripped) false (Idle) | Used to trigger localized energy/lighting management (e.g., wake up room variables upon exit). |
| Emergency / Fire Input | BooleanPoint or NumericPoint | true (Emergency Alarm) false (Normal) | Tied directly to a high-priority Niagara Alarm Class. Must bypass normal delays. |

Option B: Direct OpenAccess API (WebSockets)

Because REST API polling is too slow to reliably capture a momentary REX button press, a real-time WebSocket stream is required.

- Subscription: Niagara establishes a secure WebSocket connection (wss://) and subscribes specifically to hardware input status changes (InputStateChanged events).

- Data Payload Example: The incoming JSON payload contains the InputID, InputName, PanelID, and the numeric state index representing the circuit.

- Parsing Script: A Niagara Web Services/JSON module parses the message string and instantly updates a corresponding virtual point block.

Approved occupancy and person-event integration:

For LenelS2 OnGuard → Niagara occupancy and person-event integration, I recommend separating occupancy data from person-identifiable access events, because they have different security and privacy implications.

Functional requirement

The integration shall make approved occupancy information and authorized person-event information from LenelS2 OnGuard available to Niagara. Only information explicitly approved for Niagara integration shall be exposed, and the integration shall not provide cardholder or personally identifiable information unless specifically authorized.

1. Occupancy information

Niagara may receive occupancy information for configured areas/zones, where supported by the OnGuard implementation.

Recommended points:

Area / Zone

├── CurrentOccupancyCount

├── OccupiedStatus

├── MaximumOccupancy

├── OccupancyPercentage

├── LastOccupancyUpdate

└── DataQuality

Typical values:

| Information | Niagara Type | Description |
| --- | --- | --- |
| Occupancy Count | Numeric | Current number of persons in configured area |
| Occupied | Boolean | Area occupied/not occupied |
| Maximum Occupancy | Numeric | Configured capacity, if available |
| Occupancy % | Numeric | Current occupancy relative to capacity |
| Last Update | Timestamp | Last valid occupancy update |
| Quality | Status | Good / Stale / Fault / Unknown |

For example:

Building_01

Floor_02

CurrentOccupancy = 128

Occupied         = True

Capacity         = 250

OccupancyPercent = 51.2%

2. Person-event information

Where explicitly approved, Niagara may consume access/person events such as:

Access Granted

Access Denied

Entry

Exit

Badge/Card Presented

Invalid Credential

Anti-Passback Violation

Each approved event could contain:

Event Type

Event Timestamp

Door/Reader ID

Door/Reader Name

Area/Zone

Direction (Entry/Exit)

Result (Granted/Denied)

If personally identifiable information is approved, additional fields could include cardholder/person identifier and display name. Otherwise, Niagara should receive non-person-identifiable events.

For example:

EventType   = AccessGranted

Reader      = MainLobby_Entry

Direction   = Entry

Area        = Building_01

Timestamp   = 10:32:15

PersonID    = Not Exposed

PersonName  = Not Exposed

3. Occupancy calculation

The design must establish which system is the system of record for occupancy.

Preferred:

OnGuard

│

│ Calculates/Maintains

▼

Occupancy

│

│ Integration

▼

Niagara

│

▼

BMS Visualization / Analytics

If OnGuard already maintains occupancy, Niagara should consume the OnGuard value rather than independently calculating it from access events.

If Niagara must calculate occupancy:

Valid Entry  → Count +1

Valid Exit   → Count -1

This approach needs additional handling for missed events, tailgating, emergency exits, controller outages, event duplication and synchronization after Niagara restarts.

4. Privacy/security requirement

Because person-event information can contain personally identifiable information, include a specific requirement:

The integration shall expose only approved person-event attributes to Niagara. Personally identifiable cardholder information, including person name, credential/card number, employee ID, photograph and other cardholder attributes, shall not be transferred unless explicitly authorized by the customer and permitted by the OnGuard integration account.

Recommended final requirements

You can put these directly into the functional requirements:

Occupancy:

The integration shall make approved occupancy information from LenelS2 OnGuard available to Niagara for configured areas/zones, including current occupancy count, occupied/unoccupied state, and associated timestamp and data-quality information where supported.

Person Events:

The integration shall make approved person/access-event information from LenelS2 OnGuard available to Niagara, including event type, event timestamp, reader/door, area and entry/exit direction where available. Person-identifiable information shall only be exposed when explicitly approved and authorized.

Key technical questions for Lenel

Before implementing the Niagara driver, these should be confirmed with Lenel/OpenAccess:

- Which OpenAccess API objects/endpoints provide door physical state, lock state, reader state and controller state?

- What exact event types/event IDs represent Door Open, Door Closed, Forced Open and Held Open?

- Is lock state exposed as a directly queryable property, an event, or both?

- Which reader/controller hardware health states are exposed through OpenAccess?

- Which security alarms can be subscribed to?

- How are alarm active, clear, acknowledge and reset represented?