Based on all eight screenshots, this PRD is defining a read-only integration from LenelS2 OnGuard / S2 NetBox into Tridium Niagara 5. Niagara is intended to consume access-control events, door/controller states, alarms, and approved occupancy/person information, then use that information for visualization, alarms, analytics, occupancy logic, HVAC/lighting response, and orchestration.

The most important architectural rule is:

LenelS2 remains the authoritative system for access control. Niagara consumes approved data and does not administer cards, credentials, permissions, schedules, doors, or access-control policy.

That has a major impact on how the Niagara driver should be designed.

1. What the PRD is trying to build

The architecture shown in the screenshots is essentially:

Lenel OnGuard / S2 NetBox

System of Record

|

|

OpenAccess / Approved API

|

v

Niagara Lenel Driver

|

+-------------+-------------+

|             |             |

v             v             v

Events         Status      Occupancy

|             |             |

+-------------+-------------+

|

v

Niagara Points

|

+-----------+-----------+

|           |           |

v           v           v

Alarm       History     Analytics

|

v

HVAC / Lighting

The direction is explicitly:

LENEL ONGUARD / S2 NETBOX

|

v

NIAGARA 5

and not:

NIAGARA

|

X

v

LENEL

The PRD even states that Niagara-to-LenelS2 commands are outside the product scope.

2. Problem the PRD is addressing

Today, security/access control and building automation appear to operate independently.

For example, Lenel knows:

John badge entered Building A

Door A-101 opened

Door A-101 forced open

Last employee left Building A

while Niagara knows:

AHU operating

Room temperature

Lighting status

Energy consumption

Occupancy schedule

Without integration, an operator or another application has to correlate those two worlds.

With the driver:

Badge Event

|

v

Lenel

|

v

Niagara Driver

|

+--> Occupancy = Occupied

|

+--> HVAC occupied mode

|

+--> Lighting occupied mode

Likewise:

Last Access Event / Occupancy = 0

|

v

Niagara

|

v

Building setback mode

|

+----+----+

|         |

HVAC    Lighting

setback      off

That is the business value of the integration.

3. Data that Niagara must receive

The screenshots identify approximately six major data groups.

| Data Category | Example | Niagara usage |
| --- | --- | --- |
| Access decision events | Access Granted / Access Denied | Visualization, occupancy, analytics |
| Door states | Open, Closed, Held, Forced | Alarm and supervisory monitoring |
| Reader/controller status | Online/offline/fault | Equipment health monitoring |
| Lock/security alarms | Door alarm, security alarm | Niagara alarms |
| REX/emergency input | Request-to-Exit, emergency input | Security/building context |
| Security mode changes | Threat level/security mode | Building operational response |
| Occupancy/person events | Approved person/access activity | Occupancy/HVAC/lighting |

The wording approved person information is important.

It does not necessarily mean that Niagara should receive full cardholder records.

For example, Niagara may receive:

PersonId = 29391

Door = Lobby Entrance

AccessResult = Granted

Time = 10:25:11

rather than:

Name

Home Address

Email

Phone

Badge credential

Access levels

PIN

The technical design needs to determine exactly which fields are permitted.

4. Data ownership model

This section is particularly important for the driver architecture.

The PRD establishes something like this:

| Domain | Authoritative system | Niagara responsibility |
| --- | --- | --- |
| Cardholders / credentials | LenelS2 | Consume approved attributes only |
| Access levels / permissions | LenelS2 | No administration/write-back |
| Access/door events | LenelS2 | Consume, normalize, alarm, history, analyse |
| Security alarms/threat status | LenelS2 | Consume approved states |
| HVAC / lighting / energy / BAS | Niagara | Niagara owns these |
| Building analytics | Niagara | Correlate security + building information |

This means the Niagara driver should not replicate the Lenel database.

Avoid a model like:

Niagara

└── Cardholders

├── Person1

├── Person2

├── Person3

└── ...

unless Lenel and the security/privacy teams specifically authorize it.

A better model is event/status-oriented:

LenelNetwork

|

+-- Site01

|

+-- Controllers

|

+-- Readers

|

+-- Doors

|

+-- SecurityPoints

|

+-- Occupancy

5. Functional requirements from the PRD

The screenshots show FR-01 through FR-11.

FR-01 — Access granted / denied

Niagara must receive:

ACCESS_GRANTED

ACCESS_DENIED

Typical event data could be:

AccessEvent {

eventId

eventType

timestamp

personId

doorId

readerId

controllerId

accessResult

reasonCode

}

This should probably be implemented as an event stream, rather than simply polling a point every few seconds.

Otherwise events can be missed.

FR-02 — Door states

Niagara must expose:

OPEN

CLOSED

FORCED

HELD

A Niagara representation might look like:

Door_101

doorState

forcedOpen

heldOpen

lastStateChange

communicationStatus

The driver should distinguish between:

Physical state

Alarm condition

Event

For example:

Door Open

is not automatically equivalent to:

Door Forced Open

6. Reader and controller health

FR-03 says reader/controller status must be available.

This should probably become Niagara health points such as:

Controller_01

├── status

├── communicationStatus

├── lastSeen

├── firmware

└── fault

Reader_01

├── status

├── communicationStatus

└── lastEvent

Possible values might include:

ONLINE

OFFLINE

FAULT

UNKNOWN

The exact values must come from Lenel's API.

Do not invent a Niagara enumeration and assume Lenel returns the same states.

Create a normalization layer.

For example:

LenelControllerState

|

v

StateNormalizer

|

v

NiagaraHealthState

7. Lock states and security alarms

FR-04 requires lock status and security alarms.

These are two different concepts.

A door could be:

Door state    = CLOSED

Lock state    = LOCKED

Alarm state   = NORMAL

or:

Door state    = OPEN

Lock state    = UNLOCKED

Alarm state   = HELD_OPEN

or:

Door state    = OPEN

Lock state    = LOCKED

Alarm state   = FORCED_OPEN

So don't create one generic status point.

A better model would be:

Door

├── doorState

├── lockState

├── alarmState

├── communicationStatus

└── lastEvent

8. Request-to-Exit and emergency inputs

FR-05 requires REX and emergency input states.

Example:

Door

|

+-- requestToExit

|

+-- emergencyRelease

|

+-- emergencyInput

Important implementation question:

Are these:

Boolean state points?

or:

momentary events?

For example, REX may occur for 500 ms.

If you poll every 10 seconds, you could completely miss it.

Therefore this is one of the areas where you should strongly consider:

Lenel event subscription

+

periodic reconciliation polling

rather than polling alone.

9. Threat level / security mode

FR-06 says threat-level or security-mode changes must become available in Niagara.

Potential examples could be:

NORMAL

ELEVATED

LOCKDOWN

EMERGENCY

but these names are only examples—the actual Lenel configuration needs confirmation.

The important point is that Niagara may use it for building operation.

For example:

Lenel Security Mode = Emergency

|

v

Niagara

|

+---+---+

|       |

HVAC   Operator

Logic    Alarm

However, because commands back to Lenel are excluded:

Niagara ---> Set Lenel Threat Level

should not be implemented.

10. Occupancy/person-event integration

FR-07 appears to be one of the most valuable requirements.

A badge event can contribute to building occupancy.

Example:

Access Granted

|

v

Direction = IN

|

v

Occupancy +1

And:

Access Granted

|

v

Direction = OUT

|

v

Occupancy -1

Then:

Occupancy > 0

|

+--> HVAC occupied

|

+--> Lighting occupied

But you should not automatically assume that access granted = actual occupancy.

There are multiple complications:

Tailgating

Badge used but person doesn't enter

Multiple people on one badge

Missing exit badge

Door configured as entrance only

Emergency evacuation

Anti-passback

Visitor badges

So occupancy logic needs a clearly defined business rule.

11. Niagara must remain consumer, not authority

FR-08 is essentially the architecture boundary.

Niagara should never become the system controlling:

Card creation

Credential creation

Badge activation/deactivation

Access levels

Door access permissions

Schedules

Security policies

That means your driver probably should not expose writable Niagara actions such as:

unlockDoor()

lockDoor()

grantAccess()

disableBadge()

modifyAccessLevel()

for this first implementation.

That gives you a cleaner and safer driver API.

12. Visualization and supervisory requirements

FR-09 says Niagara must support visualization/supervisory use.

So the driver needs to expose normalized Niagara components suitable for PX pages.

For example:

Door A101

----------------

State        CLOSED

Lock         LOCKED

Alarm        NORMAL

Controller   ONLINE

Last Event   10:32:51

The UI shouldn't need to understand Lenel-specific raw JSON/XML/API structures.

That transformation belongs inside the driver.

13. Analytics/orchestration requirement

FR-10 is where Lenel information becomes building automation information.

Example:

Lenel

Access event

|

v

Niagara Driver

|

v

Occupancy Service

|

+---+--------+---------+

|            |         |

HVAC       Lighting   Energy

This means the driver should provide clean Niagara points rather than forcing analytics applications to interrogate Lenel directly.

14. FR-11 — no Niagara → Lenel commands

This requirement deserves an explicit architecture guard.

I would implement the first driver as:

READ

SUBSCRIBE

DISCOVER

MONITOR

without:

WRITE

COMMAND

CONTROL

That minimizes both cybersecurity and access-control certification concerns.

15. Primary use cases from the screenshots

The PRD gives several useful scenarios.

| Use Case | Lenel Input | Niagara Action |
| --- | --- | --- |
| Occupancy | Badge/access event | Apply occupancy logic, HVAC/lighting response |
| Last person out | Final access/occupancy event | Set building setback mode |
| Door held/forced | Security alarm | Create BAS alarm/context/operator notification |
| After-hours access | Credential validation event | Temporarily activate HVAC/lighting |
| Emergency response | Door/security event | Provide building-wide operational response |
| Energy optimization | Actual access activity | Optimize HVAC, lighting and energy |

These tell you that the driver cannot simply expose a raw event log.

It needs to expose information in a form usable by Niagara control logic.

16. Recommended Niagara driver architecture

I would divide the module approximately like this:

lenel-rt

|

+-- LenelNetwork

|

+-- LenelDevice

|

+-- LenelPoint

|

+-- LenelDoorPoint

|

+-- LenelReaderPoint

|

+-- LenelControllerPoint

|

+-- LenelAlarmPoint

|

+-- LenelOccupancyPoint

lenel-wb

|

+-- Network Manager

+-- Discovery UI

+-- Point Manager

+-- Configuration UI

Internally:

LenelNetwork

|

+-- ConnectionManager

|

+-- AuthenticationManager

|

+-- SessionManager

|

+-- DiscoveryService

|

+-- EventSubscriptionManager

|

+-- PollingManager

|

+-- EventNormalizer

|

+-- StateCache

|

+-- ReconnectManager

|

+-- Diagnostics

17. Connection manager

It should own the API endpoint, for example conceptually:

https://onguard-server/...

with configuration such as:

host

port

TLS

authentication type

username/account

connection timeout

read timeout

subscription timeout

retry policy

You previously highlighted authentication/session handling, and that remains one of the highest-priority items to resolve before implementing the driver.

18. Authentication/session manager

Do not allow every Niagara point to authenticate independently.

Use one central session manager:

Niagara Driver

|

v

LenelSessionManager

|

+-- Authenticate

|

+-- Store session/token/cookie

|

+-- Detect expiration

|

+-- Reauthenticate

|

+-- Restore subscriptions

If OpenAccess uses a session cookie, the flow might conceptually be:

POST Authenticate

|

v

Session/Cookie

|

v

Subsequent API calls

If the session expires:

401 / authentication error

|

v

Session invalid

|

v

Authenticate

|

v

Restore event subscription

|

v

Continue

This needs confirmation from the actual OpenAccess version/documentation used in your environment.

19. Event subscription versus polling

For this integration I would use a hybrid architecture.

Event-driven

Use event subscription for:

Access granted

Access denied

Door forced

Door held

REX

Security alarm

Threat-level change

because these can be transient.

Polling

Periodically poll:

Controller health

Reader health

Door current state

Lock current state

Security mode

This is useful for reconciliation.

Architecture:

Lenel

|

+------+------+

|             |

Events          Poll

|             |

+------+------+

|

Cache

|

Niagara

That protects you against missed events after a network interruption.

20. Driver discovery

Niagara operators should not manually create hundreds of door points.

The driver should ideally support discovery.

For example:

Lenel Network

|

+-- Discover

|

+-- Controllers

+-- Readers

+-- Doors

+-- Security points

Workbench might display:

Name              Type        ID

-----------------------------------

Main Controller   Controller  182

Lobby Reader      Reader      412

Lobby Door        Door        391

East Exit         Door        392

Operator selects objects and clicks:

Add

and they become Niagara components.

21. Stable identifiers are critical

Do not use door names as identifiers.

For example:

Lobby Entry Door

can be renamed.

The driver should store something similar to:

LenelObjectId = 294829

and separately:

displayName = Lobby Entry Door

Your Niagara component can then survive Lenel name changes.

22. Event de-duplication

This should explicitly be part of the design.

Suppose Niagara disconnects and reconnects. Lenel may resend events.

Without deduplication:

Access Granted

|

v

Occupancy +1

same event resent

Access Granted

|

v

Occupancy +1

Now occupancy is wrong.

Use a stable event identifier if Lenel provides one:

eventId

timestamp

sequenceNumber

and maintain a bounded deduplication cache.

23. Connection health

The Niagara network should expose its own health.

For example:

LenelNetwork

|

+-- connectionStatus

+-- authenticationStatus

+-- subscriptionStatus

+-- lastEventReceived

+-- lastSuccessfulPoll

+-- lastError

+-- reconnectCount

Possible overall state:

OK

DEGRADED

DOWN

This is much better than simply showing the Niagara network as "faulted."

24. Data normalization

Do not allow raw Lenel representations to leak throughout Niagara.

Create a translation layer:

Lenel raw event

|

v

LenelEventMapper

|

v

NormalizedEvent

|

v

Niagara Points

For example:

enum DoorState {

OPEN,

CLOSED,

HELD,

FORCED,

UNKNOWN

}

Mapping belongs in one place.

This becomes very useful if S2 NetBox and OnGuard expose slightly different values.

25. History

You need to distinguish:

Current state

from:

Event history

For example:

doorState = CLOSED

is a current Niagara point.

But:

10:20 Door Open

10:20 Door Closed

10:42 Door Forced

10:43 Door Closed

is historical/event information.

Determine whether event history should be:

Niagara history

Niagara alarm history

external database

or only transient

before implementing the storage model.

26. Alarm handling

A Lenel event doesn't automatically need to become a Niagara alarm.

For example:

Access Granted

normally wouldn't become an alarm.

But:

Door Forced

Controller Offline

Security Alarm

probably would.

So add an alarm mapping layer:

Lenel Event

|

v

Alarm Classification

|

+---+-------------+

|                 |

Normal Event    Niagara Alarm

Also determine:

alarm class

priority

acknowledgement

reset behavior

source

text

27. Privacy/security

The PRD explicitly calls out privacy and data retention.

The driver should probably avoid exposing credentials entirely.

For example, don't log:

Card number

PIN

credential secret

authentication password

Diagnostic logs should look more like:

Event received for DoorId=391

AccessResult=Granted

rather than dumping the complete Lenel payload.

28. Version compatibility

The PRD specifically leaves this TBD:

Supported OnGuard / S2 NetBox versions

Supported Niagara 5 versions/modules

Technical architecture

That means implementation shouldn't start with assumptions such as:

Works against every OnGuard version

Your driver might eventually need a compatibility matrix:

| Component | Supported versions |
| --- | --- |
| Niagara | TBD |
| OnGuard | TBD |
| S2 NetBox | TBD |
| OpenAccess API | TBD |
| Java runtime | Niagara-dependent |

29. Questions I would send to Lenel / product owner before implementation

This is the checklist I would use in the technical RFI/workshop:

- Interface: Which interface are we required to use: OnGuard OpenAccess, S2 API, DataConduIT, OAAP-approved interface, or another SDK?

- Versions: What exact OnGuard and S2 NetBox versions must the Niagara driver support?

- Niagara versions: Which Niagara 5 releases/JACE platforms are targeted?

- API documentation: Can Lenel provide the exact API/SDK documentation matching the deployed versions?

- Integration account: Will Niagara receive a dedicated machine/service account?

- Authentication: Does the selected Lenel interface use internal credentials, Windows/SSO, API key, token, session cookie, client certificate, or another mechanism?

- Session lifetime: What is the configured session/token lifetime and idle timeout?

- Session renewal: Can sessions be refreshed, or must Niagara fully reauthenticate?

- Concurrent sessions: Can several Niagara stations/JACEs authenticate using the same integration account?

- Credential rotation: What is the credential/password/certificate rotation process?

- TLS: What TLS versions and cipher requirements apply?

- Certificates: Are server/client certificates required, and how should Niagara trust/store them?

- Endpoint configuration: What host, port, context path and API version should the driver use?

- HA: Is OnGuard/OpenAccess deployed in high availability, and does Niagara need primary/secondary endpoints?

- Failover: Does failover occur through DNS/load balancer, or must the Niagara driver switch endpoints?

- Events: Does the API support real-time event subscription, streaming, callback, long polling, or websocket-style delivery?

- Subscription lifecycle: How is an event subscription created, renewed and terminated?

- Subscription reconnect: After session expiration or network failure, must Niagara recreate the event subscription?

- Replay: Can missed events be requested after reconnection?

- Event cursor: Is there an event ID, sequence number or cursor Niagara can persist for replay?

- Ordering: Are events guaranteed to arrive in chronological/sequence order?

- Duplicates: Can events be delivered more than once?

- Retention: How long does Lenel retain events available to API clients?

- Rate limits: Are there API call, event subscription, throughput or concurrent-connection limits?

- Volume: What is the expected normal and peak event rate?

- Scale: How many panels, controllers, readers, doors and cardholders exist at the largest targeted site?

- Door states: What exact values represent open, closed, held and forced?

- Lock states: What exact lock-state values are available?

- Alarm states: Which security alarm types must Niagara expose?

- Controller health: What controller health/status values are available?

- Reader health: What reader status values are available?

- Communication state: Can Niagara distinguish controller offline, reader offline, API unreachable and OnGuard server unavailable?

- REX: Is Request-to-Exit represented as a persistent point or momentary event?

- Emergency inputs: Which emergency-input types are in scope?

- Threat/security mode: What are the valid threat/security-mode states?

- Access-event fields: Which fields accompany Access Granted and Access Denied events?

- Denied reason: Are access-denied reason codes available?

- Person data: Exactly which person/cardholder attributes are approved for Niagara?

- Credential data: Can we explicitly confirm that raw credential/card/PIN data must never enter Niagara?

- Privacy: Are person names allowed, or should Niagara use only anonymous/internal person IDs?

- Occupancy: Does Lenel provide calculated occupancy, or is Niagara expected to derive it?

- Direction: How does Niagara determine whether a reader represents IN or OUT?

- Last-person-out: Does Lenel provide a native last-person-out event/state, or must Niagara calculate it?

- Anti-passback: Is anti-passback information available and should it influence occupancy?

- Occupancy correction: How is occupancy corrected after missed events, tailgating, emergency exits or system restart?

- Discovery: Does the API provide enumeration/discovery for panels, controllers, readers and doors?

- Identifiers: What immutable ID should Niagara persist for each Lenel object?

- Renaming: If a Lenel object is renamed, does its immutable ID remain unchanged?

- Deletion: How will Niagara detect that a Lenel object has been deleted or disabled?

- Hierarchy: What is the Lenel hierarchy—system/site/panel/controller/reader/door—and should Niagara mirror it?

- Polling: Which states should be periodically polled even when event subscription is active?

- Recommended intervals: What polling interval does Lenel recommend?

- Bulk APIs: Are batch APIs available to avoid one request per door/controller?

- Initial synchronization: What endpoints should Niagara call during startup to establish current state?

- Reconnect synchronization: What data should be refreshed after reconnection?

- Alarm acknowledgment: Is alarm acknowledgement strictly read-only from Lenel, or does Niagara need independent BAS acknowledgement?

- Alarm clearing: How does Lenel indicate that a forced/held/security alarm has returned to normal?

- History: Which Lenel data must Niagara historize?

- Retention: What Niagara history retention is required?

- Timestamps: Are timestamps UTC or local time?

- Time zones: Does each Lenel site contain timezone information?

- Clock synchronization: Are OnGuard and Niagara required to use a common NTP source?

- Audit: What integration actions/events must be audit logged?

- Logging: Which Lenel payload fields are prohibited from Niagara diagnostic logs?

- Encryption: Are there encryption-at-rest requirements for cached person/event information?

- Caching: How much Lenel information may Niagara cache locally?

- Persistence: Should the event cursor/state cache survive Niagara station restart?

- Read-only enforcement: Should Niagara completely omit write APIs/actions or merely disable them by configuration?

- Future scope: Is door lock/unlock/write-back intentionally excluded permanently, or only from V1?

- Certification: Does this integration need Lenel/OAAP certification before release?

- Development environment: Will a Lenel development/test server be provided?

- Simulator: Is an API simulator/event generator available?

- Test credentials: Will test accounts/cards/readers/doors be provided?

- Fault testing: How should we simulate controller offline, reader offline, forced door, held door and OpenAccess outage?

- Performance criteria: What maximum event-to-Niagara latency is acceptable?

- Recovery criteria: After API outage, how quickly must Niagara recover?

- Data-loss criteria: Is any loss of access events acceptable?

- Commissioning: What site acceptance test cases are mandatory?

- Security review: What cybersecurity/security-architecture approval is required?

- Documentation: Who owns the final interface-control document and approved field mapping?

30. Questions that should block coding

Although all 80 questions matter, I would treat these as implementation blockers:

Exact Lenel API/interface

|

Authentication/session mechanism

|

Event subscription mechanism

|

Supported versions

|

Object IDs/data schema

|

Reconnect/event replay behavior

|

Person/privacy fields

|

Expected scale/event rate

Until those are answered, you can build the Niagara framework skeleton, but not safely complete the integration.

31. Suggested implementation sequence

I would build the driver in this order:

Phase 1

LenelNetwork

Connection

Authentication

Session management

Health monitoring

↓

Phase 2

Device discovery

Controller/Reader/Door model

↓

Phase 3

State polling

Door/Lock/Controller/Reader status

↓

Phase 4

Event subscription

Granted/Denied

Held/Forced

REX

Security alarms

↓

Phase 5

Reconnect

Replay

Deduplication

Reconciliation

↓

Phase 6

Niagara alarm/history

↓

Phase 7

Occupancy calculation

↓

Phase 8

HVAC/Lighting analytics use cases

↓

Phase 9

Cybersecurity + performance testing

↓

Phase 10

Commissioning / OAAP validation

The key design principle is to make the Niagara driver a reliable event/status adapter, not a second access-control system. If you get the connection/session layer, event replay/deduplication, stable object IDs, and normalization model right, the later Niagara PX, alarm, history, and HVAC/occupancy use cases become much easier to implement.